# Mechanical Specifications

SERIES CAS CLOSETLINE (WATER SOURCE) (GROUND SOURCE) HEAT PUMPS

PART 1 GENERAL

  - SECTION INCLUDES

# A. Horizontal and Vertical Packaged Water Source Heats

  - RELATED SECTIONS

  - REFERENCES

- ETL Listed under Underwriters Laboratories Standard for Safety UL1995 for heat pumps.

- AHRI ISO Standard 13256-1

  - DELIVERY, STORAGE AND HANDLING

- Deliver products to site, store and protect from the weather and construction debris and be tagged with model number, configuration, and (OPTION) site location.

  - ENVIROMENTAL REQUIREMENTS

- Protect units from construction debris by covering all openings prior to start-up of the equipment.  Units must not be used for heating, cooling, or ventilation prior to the start-up of equipment for permanent use.  Use of the equipment for the temporary heating, cooling or ventilation is prohibited.

  - FACTORY TESTING

## All units shall be factory tested at normal operating conditions.  Cabinets and fans shall be tested to verify proper fan and control operation.  Refrigeration chassis shall be factory tested with cataloged water flow rates and sequenced to verify the proper operation of safety controls.  Testing without utilizing cataloged water flow rates is unacceptable.

  - SUBMITTAL DOCUMENTATION

- Standard submittals shall include capacities, drawings, electrical data, installation, operation and maintenance manuals and other details.

PART 2 PRODUCTS

  - TYPE

- Vertical and Horizontal (Water Source) (Ground Source) Heat Pump with, discharge arrangements, hose kits, and all accessories.  Units shall be (water source 60°F to 95°F (15.6°C to 35°C)) (ground source 20⁰F to 120⁰F (‒6.7⁰C to 48.9⁰C)) entering fluid temperature for (water source) (ground source)  heat pump applications.

  - CAPACITY

- Shall be as indicated on the drawings, which are based on Whalen units.  Capacities shall be certified under AHRI ISO Standard 13256-1.

  - CABINETS

- The unit cabinet shall be fabricated of 18 Gauge G60 galvanized steel, and service panels shall be fabricated of 22 Gauge G60 galvanized steel.  All welded assemblies are treated to prevent corrosion.

- The cabinet shall be insulated with 1/2-inch thick 2-pound density thermal and acoustical fiberglass insulation meeting material standard ASTM-C1071 and have an integral water repellent.  The insulation shall have a fungi and bacteria resistant barrier with no growth conforming to ASTM-C1338, ASTM G21 and ASTM G22 and meet fire safety standards under NFPA90A and NFPA90B. (OPTION 1) 1/2-inch 1-1/2-pound density foil faced thermal and acoustical fiberglass insulation. (OPTION 2) 1/2-inch closed cell thermal and acoustical fiberglass insulation

- Cabinet return and discharge air openings shall be factory cut and flanged on all sides.   .

- Hanging brackets shall be provided on all horizontal units and shall be integral to unit construction.  Screw on style brackets are not acceptable.

- (OPTION) A factory installed vibration isolation pad shall be installed on the bottom of vertical units.

  - REFRIGERATION SYSTEM

- The refrigeration system consists of the compressor, air coil, water coil, reversing valve, expansion device, filter-drier, and safety controls. System components shall be designed for easy field service accessibility

- The compressor shall be the sealed hermetic type approved and tested for reverse cycle operation.  Internal thermal overload protection shall be provided.  The compressor shall be internally dual isolated.  Compressor motors shall be permanent split capacitor (PSC) type.

- The air coils shall be copper tubes mechanically bonded to aluminum fins, multi-circuited to insure maximum coil distribution and effectiveness.  The coil shall be rated to withstand 600 psig refrigerant working pressure.   Face velocity shall not exceed 400 feet per minute to insure quiet operation and positive condensate drainage.

- The water coils shall incorporate an electro-coated steel outer tube and a copper inner tube.  The inner tube shall be spirally fluted and bonded to the outer tube to insure controlled refrigerant velocity and distribution. The coil shall be rated to withstand 650 psig refrigerant and 400 psig fluid working pressures.  (OPTION) Provide Cupro-nickel COAX coil.

- The reversing valve shall be 4-way electric type, pilot operated for quiet reversal.

- (OPTION) Automatic flow control valve – An automatic flow control valve shall be provided with each unit and be factory preset for a fixed flow rate regardless of system pressure.  Each automatic balancing valve shall be capable of operation over a pressure differential range of 2 to 80 PSID and be easily accessible for cleaning and maintenance.

- (OPTION1) Standard Two-way, two-position (On/Off) control valve (30 psi differential pressure) – A two-way, two-position (On/Off) electric control valve may be factory or field mounted and wired unit.

(OPTION2) High Pressure Two-way, two-position (On/Off) control valve (60 psi differential pressure) – A two-way, two-position (On/Off) electric control valve may be factory or field mounted and wired unit.

  - WATER CONNECTIONS

- Entering water, leaving water, and condensate drain connections shall be FNPT.

- (OPTION 1) Water connections shall be accomplished via an Insta-Lock™ quick connect accessory hose kit consisting of synthetic yarn-reinforced EPDM core hose surrounded by a 304 stainless-steel braid. Hose kit shall have brass fittings with stainless-steel locking balls and EPDM seals. Hose ends shall have colored bands to indicate supply or return water as well as colored indicator to verify locking status which connects to Insta-Lock™ fitting on entering water and leaving water connections. Threaded connections with or without sealing washers are not permitted. The hose kit shall be rated for maximum working pressure of 750 psi and minimum burst pressure rating of 2250 psi.

  - DRAIN PAN

- The drain pan shall collect and drain condensate that may form from any component internal to the heat pump and shall be fabricated of welded and soldered 20 Ga. 304 stainless steel.  Vertical equipment is internally trapped, horizontal equipment require an external trap, the copper condensate drain shall be rolled and soldered into the pan.

  - FANS

- The fan shall be slow speed forward curved centrifugal type capable of two fan speeds, and shall be accessible for removal and maintenance through the service panels.

  - MOTORS

- Fan motors shall be of the permanently lubricated PSC standard, as required; suitable for the current characteristics shown on the drawings, and shall have built-in thermal overload protection.

- (OPTION: fan motors shall be of the permanently lubricated constant-torque ECM type, suitable for the current characteristics shown on the drawings, and shall have built-in overload protection.

- Motors shall be plug-in, multi-speed type.

  - SUPPLY GRILLES

- The supply grilles shall be of the single deflection type fabricated of clear anodized aluminum.  All supply openings shall be painted black with a damper assembly and sight baffle provided when one unit is serving two separate rooms.

(OPTION 1) The supply grilles shall be of the single deflection type fabricated of (factory white painted extruded aluminum) or (custom painted extruded aluminum) (SELECT ONE).  All supply openings shall be painted black with a damper assembly and sight baffle provided when one unit is serving two separate rooms.

(OPTION 2) The supply grilles shall be of the double deflection type fabricated of (clear anodized extruded aluminum), (factory white painted extruded aluminum) or (custom painted extruded aluminum) (SELECT ONE).  All supply openings shall be painted black with a damper assembly and sight baffle provided when one unit is serving two separate rooms.

  - FILTERS

## (STANDARD) Filters shall be 1” thick disposable fiberglass media, MERV 4.

(OPTION 1) Filters shall be 1” thick disposable pleated media, MERV 8.

(OPTION 2) Filters shall be 1” thick disposable pleated media, MERV 11

(OPTION 3) Filters shall be 1” thick disposable pleated media, MERV 13

(OPTION 4) Filters shall be 2” thick disposable pleated media, MERV 8

(OPTION 5) Filters shall be 2” thick disposable pleated media, MERV 11

(OPTION 6) Filters shall be 2” thick disposable pleated media, MERV 13.

  - POWER SUPPLY

- Single point field power connection is made to unit junction box through either of the 7/8" knockouts located on the side of the cabinet as shown on the drawings.

(OPTION 1) Each unit shall include a non-fused disconnect switch, factory mounted and wired.

(OPTION 2) Each unit shall include a supplemental overcurrent protection switch, factory mounted and wired.

  - CONTROLS

          - Unit shall include a solid-state control board as part of the unit control system incorporating these features:

          - Random start compressor protection.  Anti-short cycle compressor minimum OFF time delay.  Safety controls that protect the compressor from the following conditions:

            - High pressure

            - Low pressure (Loss of Charge Protection)

            - Low airflow

            - Low liquid flow

            - Low entering air temperature

            - Brown-out power conditions

            - Condensate Overflow Protection

            - Low liquid temperature protection with three different settings based on liquid properties.

          - Status LED indicating the device causing a fault condition.

          - Soft lockout feature that provides for an automatic reset prior to the initiation of a hard lockout.

          - Test mode capability with shortened time delays for servicing.

  - THERMOSTAT

- The heat pump manufacturer shall provide a 24-volt manual changeover wall thermostat with a HEAT-OFF-COOL system switch and AUTO-ON fan selector switch.

- Thermostats shall be remote mounted and wired in the field.  (OPTION: factory wired thermostat extension permitting thermostat installation by plugging into the control wiring with a polarized male-female plug after the walls are finished when unit mounted.  High voltage, return air thermostats with remote bulbs subject to damage during routine service will not be accepted.

  - SPARE PARTS

- Intentionally Left Blank

## PART 3	EXECUTION

  - INSTALLATION

- Furnish as shown on the drawings and as specified herein, vertical and horizontal (water source) (ground source) heat pumps, and with capacity and electrical characteristics as scheduled.  Units shall be Series CAS as manufactured by The Whalen Company of Easton, MD.

- Install in accordance with manufacturer's installation instructions and maintain manufacturer's recommended clearances for the unit and accessories.

- Follow manufacturer's recommendations for cleaning and flushing.